## PRFI Log
Project - EPC Public Health South Phase 2 Building Improvement
RFP Bid
|  |  | Pre-Construction Request for Information (PRFI) # 2 |  | ELDER ISSUE DATE: | 2023-02-10
Item No. | Specification / Drawing Ref. No. | Description / Question | Responsible Firm | Architect/Consultant/Owner/Contractor Status/Action/Comments | Date Required | Date Completed
01 | N/A | Temporary Utilities
|  | Please confirm that since this is an existing building we can connect to existing house utilities for temporary construction facilities (i.e. water, power and gas). | 51EC, AND OTHERS | On a purely engineering basis, we do not see a problem with using the existing MEP services for temporary utilites. However this is a multi-tenant building so contractor shall verify service is part of the scope of work of the project prior to using as temp service. Regarding contractural, owner, arch. or owner represenitive shall be consulted. |  | 2023-02-14
02 | General Terms | Tax Exemption
General Terms and Conditions item 2.3.2 states: "Contractors shall not include federal, state, or local excise or sales taxes in prices offered, as the County is exempt from payment of such taxes." Then states: "Materials purchased directly by the Contractor in conjunction with this contract will, however, be subject to applicable state and local sales taxes. These taxes shall be borne by the contractor." Please confirm that this project is tax exempt.
03 | Specifications | GC Response Submittal Requirements
Specification references a "Response Submittal Requirements" page. We could not locate a document with this title. Are we missing something?
04 | A1.2 | Floor Covering Removal
Demolition note 11 calls to remove existing floor finish at Conference 129. Job walk revealed the floor finish has already been removed at this room. Reference image below. We assume no additional floor removal is required at room 129. Please confirm or clarify if otherwise.
05 | A1.2 A1.6 | Wainscot Removal
Floor plan A1.6 indicates construction note 15 at room 129 (orange peel texture above where wainscots are removed). Demolition plan A1.2 does not call for removal of wainscot outside of a single location where there is a conflict with a new light switch (note 5 on A1.2). Please review and clarify if all wainscot is to be removed in 129 Conference/Workstations. If so, please update demolition plan.
06 | A2.0 | Existing Hardware Verification or Replacement
Door schedule indicates several doors require review of existing hardware and functions and replacement if required. For bidding purposes, we would suggest all GC's carry a specified allowance for this scope.
07 | A1.1 A2.0 | Door 133A Hardware
Demolition note 2 calls to remove door handle and locket from doors to rooms 125 ad 124 for reuse at new Lactation room. Door no. 133A (IT/Storage) is the only door that calls for reuse of existing hardware. Please clarify if this salvaged hardware is intended to be reused on door no. 133A.
08 | A1.5 A2.0 | Door 100A
|  | Floor plan A1.5 indicates construction note 33 (new ADA push button) at door 100A and does not indicate a snap on frame. Door schedule does not indicate automatic door opener but does show a snap on frame. Please review and clarify if door no. 100A requires a new automatic opener and/or a snap on door frame. | 51EC, AND OTHERS | PLEASE NOTIFY MEP REGARDING FINAL DECISION. ELECTRICAL SHOWS AUTOMATIC ADA OPENER. |  | 2023-02-14
09 | A1.5 A2.0 | Door 106A
Floor plan A1.5 indicates construction note 1 (snap on door frame) at door 106A. Door schedule does not indicate this scope for this door. Please review and clarify if door no. 106A requires a snap on door frame.
10 | A2.0 | Door 107A
Door schedule on A2.0 indicates door no.107A has an existing frame. Please confirm door no. 107A does not require a new door frame.
11 | A1.5 A2.0 | Door 116A
Floor plan A1.5 indicates construction note 1 (snap on door frame) at door 116A. Door schedule does not indicate this scope for this door. Please review and clarify if door no.116A requires a snap on door frame.
12 | A1.6 A2.0 | Door 132A
Floor plan A1.6 indicates construction note 34 (replace storefront system) at door 132A. Door schedule indicates this is an existing door that requires a new automatic opener and verification of existing hardware. Please review and clarify if door no. 132A is new or existing.
13 | A1.5 A1.6 | Automatic Door Operators
|  | Please confirm that door no. 100A and 132A require automatic operators on one leaf, not two. | 51EC, AND OTHERS | PLEASE NOTIFY MEP REGARDING FINAL DECISION. ELECTRICAL SHOWS AUTOMATIC ADA OPENER. |  | 2023-02-14
14 | A2.0 | Door 134A and 134B
The door schedule lists door no. 134A and 134B as door type C “glass”. The elevation of door type C calls for hollow metal with a full glass panel insert (see image below). Please clarify if door no. 134A and 134B are intended as storefront doors (anodized aluminum) or hollow metal with a full glass panel.
15 | 17/A5.0 A1.6 | Base Cabinet at Reception 132
A base cabinet/countertop is shown behind the new reception desk in East Lobby 132 on 17/A5.0. See image below for reference. Please provide elevation with desired finishes for the base cabinet and countertop at East Lobby 132.
16 | A1.9 A2.0 | Finish Schedule vs Floor Finish Discrepancies
There seem to be discrepancies between the finish floor plan and the room finish schedule. 1. Hallway 122 - LVT-1 hatch; finish schedule CPT-1 2. Office 124 - No hatching; finish schedule CPT-1/RB-1 3. Conference 127 - No hatching; finish schedule CPT-1 4. Men's 131 - finish schedule RB-1 but Women's has no work 5. Hallway 134 - LVT-1 hatch; finish schedule CPT-1/LVT-1 Please review and clarify.
17 | A1.6 | Re-Carpet Stage
Construction note 17 calls to re-carpet rolling stage pieces, verify in field. Please provide square footage of stage to be recarpeted for bidding purposes. If this is not available, please specify an allowance for all GC's to carry.
18 | A2.0 | Acoustical Ceiling System Specification
Please provide a basis of design for the new acoustical ceiling at 132 East Lobby.
19 | A1.1 | Patching and Painting Allowance
Demolition note 3 on sheet A1.1 calls for patching and repairing existing walls. Since the level of patch/repair varies throughout the facility, for bidding purposes, we would suggest all GC's carry a specified allowance for this scope.
20 | A1.6 A1.10 | Accent Wall at Conference/Workstation 129
Floor finish plan A1.10 calls for accent wall at North wall of Conference/Workstation 129. Finish schedule and floor plan A1.6 Construction note 14 (accent wall) is called out at East and West walls. We assume accent walls are to be at East and West walls of Conference/Workstation 129. Please confirm or clarify if otherwise.
21 | A1.6 A1.10 | Accent Wall at East Lobby 132
Construction note 21 (accent wall) is called out West wall of East Lobby 132. Finish schedule and floor finish plan do not indicate this accent wall. Please clarify if accent wall is required at East Lobby 132.
22 | A1.6 A1.10 | Accent Wall at Hallway 134
Construction note 21 (accent wall) is called out East wall of Hallway 134. Finish schedule and floor finish plan do not indicate this accent wall. Please clarify if accent wall is required at Hallway 134.
23 | A2.0 | Painting Doors/Frames
Door schedule lists existing door and frame finishes (stain wood doors and paint frames). Please clarify if existing doors and frames require paint/stain.
24 | A1.5 MD-H-101.S | New Thermostat
|  | Construction note 7 calls for a new thermostat at 117 Exam Room. This scope is not indicated on the mechanical plan MD-H-101.S. Please review and clarify scope. | 51EC, AND OTHERS | WE BEILIEVE THIS IS A LEFT OVER NOTE TO PREVIOUS SCOPE OF WORK. ORIGINALLY WE HAD AN INDEPENDENT UNIT FOR ROOM 117. THIS WAS ELIMINATED DURING VE SESSION. THE EXISTING SYSTEM WILL REMAIN AS IS AND ROOM 117 WILL NOT DETERMINE THE TEMPERATURE OF ALL THE ROOMS ON THE SYSTEM. THEREFORE, WE DO NOT NEED A NEW T-STAT IN ROOM 117. |  | 2023-02-14
25 | MD-H-101.S | Existing RG Removal
|  | Demolition note 3 on MD-H-101.S calls for testing and verifying existing wall heater. This note is associated with existing registered grilles in room 129. We assume the existing return grills are to be removed and replaced. Please confirm or clarify if otherwise. | 51EC, AND OTHERS | PER OWNER AND EPC FACILITY PERSONELL REQUEST THERE IS AN EXISTING UNIT HEATER IN THE VESTIBULE THAT HASN'T WORKED THEY WANTED TO HAVE THIS CHECKED OUT AND FIXED. IF CONTRACTOR IS VERIFYING THIS IS A SUPPLY DUCT, THE DRAWINGS NOTE REGARDING THE UNIT HEATER MAY NEED TO BE DELETED. MECHANICAL WILL COORDINATE WITH OWNER AND VERIFY IF THIS IS A UNIT HEATER OR SUPPLY DUCT AND WILL REFLECT ON THE DRAWINGS AS SUCH. SUGGEST THIS GOES DOWN AS AN ADD/ALT UNTIL CLARIFIED. |  | 2023-02-14
26 | A1.4 ED-L-101.S | Lighting Demolition
|  | RCP note 16 on sheet A1.4 calls for removal and return of existing pendant lights. These are not indicated on the electrical lighting demolition plan (ED-L-101.S). We assume these need to be removed per Architecture plan, please confirm or clarify if otherwise. If correct, please update electrical demolition plan. | 51EC, AND OTHERS | NOT AWARE OF PENDANTS A1.4 ARE REFERENCING. WILL GET WITH ARHCITECTRUAL TO DTERMINE IF IN SCOPE OR PART OF PREVIOUS SCOPE WHICH WAS ELIMINATED. |  | 2023-02-14
27 | A1.4 ED-L-101.S | Lighting Demolition
|  | RCP note 10 on sheet A1.4 calls for removal of (4) light fixtures near new lactation room. Demolition note 8 on ED-L-101.S calls for removal of (2) light fixtures at this same location. See images below for reference. We assume removal of (2) fixtures per electrical is correct. Please confirm or clarify if otherwise. | 51EC, AND OTHERS | WE DID CONFIRM THE TROFFERS AND THE RECESSED LIGHTING. WE WERE SAVING MONEY AND NOT REMOVING/RELOCATING IF NOT NECESSARY. ACCORDING TO OUR EXISTING PLACEMENT VS. THE NEW LAYOUT, WE BELIEVE TWO (2) LIGHTS CAN BE REUSED. WE WILL COORDINATE WITH ARCH. AND REFLECT ON PLANS ACCORDINGLY. |  | 2023-02-14
28 | A1.4 ED-L-101.S | Lighting Demolition
|  | RCP demolition note 2 on sheet A1.4 calls for relocating new can light fixtures for new layout at Hallway 134. These fixtures are indicated as existing to remain on the electrical lighting demolition plan (ED-L-101.S). See images below for reference. Please clarify lighting scope at this location: removal and relocation in same area or leave existing as-is. | 51EC, AND OTHERS | WE DIDN'T SEE OR HEAR A REQUEST TO REMOVE OR MODIFY THE LIGHTS IN THE VESTIBULE SINCE THE SPACE REMAINS THE SAME FROM EXISTING TO NEW. WE WILL COORDINATE WITH ARCH. AND REFLECT ON PLANS ACCORDINGLY. |  | 2023-02-14
29 | ED-L-101.N E-L-101.N | Lighting Demolition
|  | Demolition note 2 (relocate fixtures) on sheet ED-L-101.N is called out at switch locations in Women's 109 and Men's 110. We assume these switches and switch leg need removal for new scope shown on E-L-101.N (new occupancy sensors) and the lighting is to remain as is. Please confirm and clarify if otherwise. | 51EC | CORRECT DUE TO THE DOOR (BELIEVE THE DOOR SWHICH CHANGES) AND THE REQUEST FROM THE ONWER, THIS BATHROOM WAS REQUESTED TO BE CONTROLLED BY OCCUPANCY SENSOR AND THEREFORE THE SWITCH AND SWITCH LEG IS DEMOLISHED. |  | 2023-02-13
29 | A1.4 E-P-101.S | New Camera Location
|  | RCP demolition note 14 on sheet A1.4 calls to relocate existing camera. Electrical plans do not indicate new location. Please review and clarify where this camera is to be relocated on the Electrical plans. | 51EC | IF CAMERA IS LOW VOLTAGE (LOWER THAN 110V) OR POWER OVER EITHERNET THEN ISN'T REQUIRED TO BE SHOWN ON ELECTRICAL (IF THIS IS THE CASE CONTRACTOR NEEDS TO CLARIFY IF THIS IS RELOCATED BY OWNER IT GROUP (THEY TYPICALLY TAKE CARE OF ALL LOW VOLTAGE CABLE/EQUIPMENT,ETC..). IF 120V WE WILL REFLECT RELOCATION ON OUR DRAWINGS. WE WILL VERIFY WITH OWNER ON VOLTAGE OF CAMERA AND RELFECT ON DRAWINGS IF REQUIRED. |  | 2023-02-14
30 | A1.4 | Analog Junction Board
|  | RCP demolition note 15 states to: "Removal analog junction board and phone wires. Verify Abandoned. Relocate if necessary." For bidding purposes, we would suggest all GC's carry a specified allowance for this scope. | 51EC | AGREE. SEE ELECTRICAL FOR ADDITIONAL INFORMATION. |  | 2023-02-13
31 | A2.0 | Substitution Request
Please review the attached information on Stanley Access Technologies Magic Force automatic door openers. Would these be an acceptable substitute to the specified LCN 4600 series openers?